## Index
Model | Label | Description | Detailed Description
701 | DER AC Measurement | DER AC measurement model.
702 | DER Capacity | DER capacity model.
703 | Enter Service | Enter service.
704 | DER AC Controls | DER AC controls model.
705 | DER Volt-Var | DER Volt-Var model.
706 | DERVolt-Watt | DER Volt-Watt model.
707 | DER Trip LV | DER Low voltage trip model.
708 | DER Trip HV | DER high voltage trip model.
709 | DER Trip LF | DER low frequency trip model.
710 | DER Trip HF | DER high frequency trip model.
711 | DER Frequency Droop | DER Frequency Droop model.
712 | DER Watt-Var | DER Watt-Var mod.
713 | DER DC Measurement | DER DC measurement.

## 701
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | Access (R/RW) | Mandatory (M/O) | Label | Description | Detailed Description
|  | DERMeasureAC | [8 empty] | DER AC Measurement | DER AC measurement model.
0 |  | ID | 701 |  | uint16 |  |  |  | R | M | DER AC Measure Model ID | DER AC measurement model id. | The model ID of the DER AC Measurement model. The value MUST be a constant value of 701.
1 |  | L |  |  | uint16 |  |  |  | R | M | DER AC Measure Model Length | DER AC measurement model length. | This pont is only valid for model instances that have a length associated with a model instance. For Modbus implementations, this point contains the total remaining length of the model in Modbus registers. Since there are no repeating elements, this point MUST be a constant value of 114.
Wiring Type
2 |  | ACType |  |  | enum16 |  |  |  | R | O | AC Wiring Type | AC wiring type.
|  | SINGLE_PHASE | 1 | [7 empty] | Single phase
|  | SPLIT_PHASE | 2 | [7 empty] | Split phase
|  | THREE_PHASE_DELTA | 3 | [7 empty] | Three phase delta
|  | THREE_PHASE_WYE | 4 | [7 empty] | Three phase wye
Operating State
3 |  | St |  |  | enum16 |  |  |  | R | M | Operating State | Operating state of the DER.
|  | OFF | 1 | [7 empty] | Off
|  | ON | 2 | [7 empty] | On
|  | FAULT | 3 | [7 empty] | Fault
|  | ERROR | 4 | [7 empty] | Error
Alarms
4 |  | Alrm |  |  | bitfield32 |  |  |  | R | M | Alarm Bitfield | Active alarms for the DER.
|  | GROUND_FAULT | 0 | [7 empty] | Ground fault
|  | DC_OVER_VOLT | 1 | [7 empty] | DC over voltage
|  | AC_DISCONNECT | 2 | [7 empty] | AC disconnect open
|  | DC_DISCONNECT | 3 | [7 empty] | DC disconnect open
|  | GRID_DISCONNECT | 4 | [7 empty] | Grid disconnect
|  | CABINET_OPEN | 5 | [7 empty] | Cabinet open
|  | MANUAL_SHUTDOWN | 6 | [7 empty] | Manual shutdown
|  | OVER_TEMP | 7 | [7 empty] | Over temperature
|  | OVER_FREQUENCY | 8 | [7 empty] | Frequency above limit
|  | UNDER_FREQUENCY | 9 | [7 empty] | Frequency under limit
|  | AC_OVER_VOLT | 10 | [7 empty] | AC Voltage above limit
|  | AC_UNDER_VOLT | 11 | [7 empty] | AC Voltage under limit
|  | BLOWN_STRING_FUSE | 12 | [7 empty] | Blown String fuse on input
|  | UNDER_TEMP | 13 | [7 empty] | Under temperature
|  | MEMORY_LOSS | 14 | [7 empty] | Generic Memory or Communication error (internal)
|  | HW_TEST_FAILURE | 15 | [7 empty] | Hardware test failure
Summary
6 |  | W |  |  | int16 |  | W_SF | W | R | O | Active Power | Total active power. | The active power being injected or absorbed in watts. The value is positive if power is being injected and negative if power is being absorbed.
7 |  | VA |  |  | int16 |  | VA_SF | VA | R | O | Apparent Power | Total active power. | The apparent power being injected or absorbed in volt-amps. The value is positive if power is being injected and negative if power is being absorbed.
8 |  | Var |  |  | int16 |  | Var_SF | Var | R | O | Reactive Power | Total reactive power. | The reactive power being injected or absorbed in volt-amps. The value is positive if power is being injected and negative if power is being absorbed.
9 |  | PF |  |  | int16 |  | PF_SF |  | R | O | Power Factor | Power factor. | The power factor as computed by xxx. [Should it be signed?]
10 |  | A |  |  | int16 |  | A_SF | A | R | O | Total AC Current | Total AC current. | The total AC current being injected or absorbed in amps. The value is positive if power is being injected and negative if power is being absorbed.
11 |  | PhPhV |  |  | int16 |  | V_SF | V | R | O | Voltage LL | Line to line AC voltage as an average of active phases.
12 |  | PhV |  |  | int16 |  | V_SF | V | R | O | Voltage LN | Line to neutral AC voltage as an average of active phases.
13 |  | Hz |  |  | int16 |  | Hz_SF | Hz | R | O | Frequency | AC frequency.
14 |  | TotWhInj |  |  | acc64 |  | TotWh_SF | Wh | R | O | Total Energy Injected | Total active energy injected (Quadrants 1 & 4).
18 |  | TotWhAbs |  |  | acc64 |  | TotWh_SF | Wh | R | O | Total Energy Absorbed | Total active energy absorbed (Quadrants 2 & 3).
22 |  | TotVarhInj |  |  | acc64 |  | TotVar_SF | Varh | R | O | Total Reactive Energy Inj | Total reactive energy injected (Quadrants 1 & 2).
26 |  | TotVarhAbs |  |  | acc64 |  | TotVar_SF | Varh | R | O | Total Reactive Energy Abs | Total reactive energy absorbed (Quadrants 3 & 4).
Temperatures
30 |  | TmpAmb |  |  | int16 |  | Tmp_SF | C | R | O | Ambient Temperature | Ambient temperature.
31 |  | TmpCab |  |  | int16 |  | Tmp_SF | C | R | O | Cabinet Temperature | Cabinet temperature.
32 |  | TmpSnk |  |  | int16 |  | Tmp_SF | C | R | O | Heat Sink Temperature | Heat sink temperature.
33 |  | TmpTrns |  |  | int16 |  | Tmp_SF | C | R | O | Transformer Temperature | Transformer temperature.
34 |  | TmpSw |  |  | int16 |  | Tmp_SF | C | R | O | IGBT/MOSFET Temperature | IGBT/MOSFET temperature.
35 |  | TmpOt |  |  | int16 |  | Tmp_SF | C | R | O | Other Temperature | Other temperature.
Phase A
36 |  | WPhA |  |  | int16 |  | W_SF | W | R | O | Watts Ph A | Active power phase A.
37 |  | VAPhA |  |  | int16 |  | VA_SF | VA | R | O | VA Ph A | Apparent power phase A.
38 |  | VarPhA |  |  | int16 |  | Var_SF | Var | R | O | Var Ph A | Reactive power phase A.
39 |  | PFPhA |  |  | int16 |  | PF_SF |  | R | O | PF Ph A | Power factor phase A.
40 |  | APhA |  |  | int16 |  | A_SF | A | R | O | Amps Ph A | Current phase A.
41 |  | VPhAB |  |  | int16 |  | V_SF | V | R | O | Phase Voltage AB | Phase voltage AB.
42 |  | VPhA |  |  | int16 |  | V_SF | V | R | O | Phase Voltage AN | Phase voltage AN.
43 |  | TotWhInjPhA |  |  | acc64 |  | TotWh_SF | Wh | R | O | Total Watt-hours Inj Ph A | Total active energy injected phase A.
47 |  | TotWhAbsPhA |  |  | acc64 |  | TotWh_SF | Wh | R | O | Total Watt-hours Abs Ph A | Total active energy absorbed phase A.
51 |  | TotVarhInjPhA |  |  | acc64 |  | TotVarh_SF | Varh | R | O | Total Var-hours Inj Ph A | Total reactive energy injected phase A.
55 |  | TotVarhAbsPhA |  |  | acc64 |  | TotVarh_SF | Varh | R | O | Total Var-hours Abs Ph A | Total reactive energy absorbed phase A.
Phase B
59 |  | WPhB |  |  | int16 |  | W_SF | W | R | O | Watts Ph B | Active power phase B.
60 |  | VAPhB |  |  | int16 |  | VA_SF | VA | R | O | VA Ph B | Apparent power phase B.
61 |  | VarPhB |  |  | int16 |  | Var_SF | Var | R | O | Var Ph B | Reactive power phase B.
62 |  | PFPhB |  |  | int16 |  | PF_SF |  | R | O | PF Ph B | Power factor phase B.
63 |  | APhB |  |  | int16 |  | A_SF | A | R | O | Amps Ph B | Current phase B.
64 |  | VPhBC |  |  | int16 |  | V_SF | V | R | O | Phase Voltage BC | Phase voltage BC.
65 |  | VPhB |  |  | int16 |  | V_SF | V | R | O | Phase Voltage BN | Phase voltage BN.
66 |  | TotWhInjPhB |  |  | acc64 |  | TotWh_SF | Wh | R | O | Total Watt-hours Inj Ph B | Total active energy injected phase B.
70 |  | TotWhAbsPhB |  |  | acc64 |  | TotWh_SF | Wh | R | O | Total Watt-hours Abs Ph B | Total active energy absorbed phase B.
74 |  | TotVarhInjPhB |  |  | acc64 |  | TotVarh_SF | Varh | R | O | Total Var-hours Inj Ph B | Total reactive energy injected phase B.
78 |  | TotVarhAbsPhB |  |  | acc64 |  | TotVarh_SF | Varh | R | O | Total Var-hours Abs Ph B | Total reactive energy absorbed phase B.
Phase C
82 |  | WPhC |  |  | int16 |  | W_SF | W | R | O | Watts Ph C | Active power phase C.
83 |  | VAPhC |  |  | int16 |  | VA_SF | VA | R | O | VA Ph C | Apparent power phase C.
84 |  | VarPhC |  |  | int16 |  | Var_SF | Var | R | O | Var Ph C | Reactive power phase C.
85 |  | PFPhC |  |  | int16 |  | PF_SF |  | R | O | PF Ph C | Power factor phase C.
86 |  | APhC |  |  | int16 |  | A_SF | A | R | O | Amps Ph C | Current phase C.
87 |  | VPhCA |  |  | int16 |  | V_SF | V | R | O | Phase Voltage CA | Phase voltage CA.
88 |  | VPhCN |  |  | int16 |  | V_SF | V | R | O | Phase Voltage CN | Phase voltage CN.
89 |  | TotWhInjPhC |  |  | acc64 |  | TotWh_SF | Wh | R | O | Total Watt-hours Inj Ph C | Total active energy injected phase C.
93 |  | TotWhAbsPhC |  |  | acc64 |  | TotWh_SF | Wh | R | O | Total Watt-hours Abs Ph C | Total active energy absorbed phase C.
97 |  | TotVarhInjPhC |  |  | acc64 |  | TotVarh_SF | Varh | R | O | Total Var-hours Inj Ph C | Total reactive energy injected phase C.
101 |  | TotVarhAbsPhC |  |  | acc64 |  | TotVarh_SF | Varh | R | O | Total Var-hours Abs Ph C | Total reactive energy absorbed phase C.
Scale Factors
105 |  | A_SF |  |  | sunssf |  |  |  | R | O | Current Scale Factor | Current scale factor.
106 |  | V_SF |  |  | sunssf |  |  |  | R | O | Voltage Scale Factor | Voltage scale factor.
107 |  | Hz_SF |  |  | sunssf |  |  |  | R | O | Frequency Scale Factor | Frequency scale factor.
108 |  | W_SF |  |  | sunssf |  |  |  | R | O | Active Power Scale Factor | Active power scale factor.
109 |  | PF_SF |  |  | sunssf |  |  |  | R | O | Power Factor Scale Factor | Power factor scale factor.
110 |  | VA_SF |  |  | sunssf |  |  |  | R | O | Apparent Power Scale Factor | Apparent power scale factor.
111 |  | Var_SF |  |  | sunssf |  |  |  | R | O | Reactive Power Scale Factor | Reactive power scale factor.
112 |  | TotWh_SF |  |  | sunssf |  |  |  | R | O | Active Energy Scale Factor | Active energy scale factor.
113 |  | TotVarh_SF |  |  | sunssf |  |  |  | R | O | Reactive Energy Scale Factor | Reactive energy scale factor.
114 |  | Tmp_SF |  |  | sunssf |  |  |  | R | O | Temperature Scale Factor | Temperature scale factor.

## 702
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | Access (R/RW) | Mandatory (M/O) | Label | Description | Detailed Description
|  | DERCapacity | [8 empty] | DER Capacity | DER capacity model.
0 |  | ID | 702 |  | uint16 |  |  |  | R | M | DER Capacity Model ID | DER capacity model id.
1 |  | L |  |  | uint16 |  |  |  | R | M | DER Capacity Model Length | DER capacity name model length.
Nameplate Ratings - Specifies capacity ratings
2 |  | WMaxRtg |  |  | uint16 |  | W_SF | W | R | O | Active Power Max Rating | Maximum active power rating at unity power factor in watts.
3 |  | WOvrExtRtg |  |  | uint16 |  | W_SF | W | R | O | Active Power (Over-Excited) Rating | Active power rating at specified over-excited power factor in watts.
4 |  | WOvrExtRtgPF |  |  | uint16 |  | PF_SF |  | R | O | Specified Over-Excited PF | Specified over-excited power factor.
5 |  | WUndExtRtg |  |  | uint16 |  | W_SF | W | R | O | Active Power (Under-Excited) Rating | Active power rating at specified under-excited power factor in watts.
6 |  | WUndExtRtgPF |  |  | uint16 |  | PF_SF |  | R | O | Specified Under-Excited PF | Specified under-excited power factor.
7 |  | VAMaxRtg |  |  | uint16 |  | VA_SF | VA | R | O | Apparent Power Max Rating | Maximum apparent power rating in voltamperes.
8 |  | VarMaxInjRtg |  |  | uint16 |  | Var_SF | Var | R | O | Reactive Power Injected Rating | Maximum injected reactive power rating in vars.
9 |  | VarMaxAbsRtg |  |  | uint16 |  | Var_SF | Var | R | O | Reactive Power Absorbed Rating | Maximum absorbed reactive power rating in vars.
10 |  | WChaRteMaxRtg |  |  | uint16 |  | W_SF | W | R | O | Charge Rate Max Rating | Maximum active power charge rate in watts.
11 |  | WDisChaRteMaxRtg |  |  | uint16 |  | W_SF | W | R | O | Discharge Rate Max Rating | Maximum active power discharge rate in watts.
12 |  | VAChaRteMaxRtg |  |  | uint16 |  | VA_SF | VA | R | O | Charge Rate Max VA Rating | Maximum apparent power charge rate in voltamperes.
13 |  | VADisChaRteMaxRtg |  |  | uint16 |  | VA_SF | VA | R | O | Discharge Rate Max VA Rating | Maximum apparent power discharge rate in voltamperes.
14 |  | VNomRtg |  |  | uint16 |  | V_SF | V | R | O | AC Voltage Nominal Rating | AC voltage nominal rating.
15 |  | VMaxRtg |  |  | uint16 |  | V_SF | V | R | O | AC Voltage Max Rating | AC voltage maximum rating.
16 |  | VMinRtg |  |  | uint16 |  | V_SF | V | R | O | AC Voltage Min Rating | AC voltage minimum rating.
17 |  | AMaxRtg |  |  | uint16 |  | A_SF | A | R | O | AC Current Max Rating | AC current maximum rating in amps.
18 |  | PFOvrExtRtg |  |  | uint16 |  | PF_SF |  | R | O | PF Over-Excited Rating | Power factor over-excited rating.
19 |  | PFUndExtRtg |  |  | uint16 |  | PF_SF |  | R | O | PF Under-Excited Rating | Power factor under-excited rating.
20 |  | NorOpCatRtg |  |  | enum16 |  |  |  | R | O | Normal Operating Category | Normal operating performace category as specified in IEEE 1547-2018.
|  | CAT_A | 1
|  | CAT_B | 2
21 |  | AbnOpCatRtg |  |  | enum16 |  |  |  | R | O | Abnormal Operating Category | Abnormal operating performance category as specified in IEEE 1547-2018.
|  | CAT_1 | 1
|  | CAT_2 | 2
|  | CAT_3 | 3
Settings - Used to adjust nameplate ratings
22 |  | WMax |  |  | uint16 |  |  | W | RW | O | Active Power Max Setting | Maximum active power setting used to adjust maximum active power rating.
23 |  | VAMax |  |  | uint16 |  |  | VA | RW | O | Apparent Power Max Setting | Maximum apparent power setting used to adjust maximum apparant power rating.
24 |  | AMax |  |  | uint16 |  |  | A | RW | O | AC Current Max Setting | Maximum AC current setting used to adjust maximum ac current rating.
25 |  | VRef |  |  | uint16 |  |  | V | RW | O | Nominal AC Voltage Setting | Nominal AC voltage setting.
26 |  | VRefOfs |  |  | uint16 |  |  | V | RW | O | Nominal AC Voltage Offset Setting | Nominal AC voltage offset setting.
27 |  | VMax |  |  | uint16 |  |  | V | RW | O | AC Voltage Max Setting | AC voltage maximum setting used to adjust AC voltage maximum rating.
28 |  | VMin |  |  | uint16 |  |  | V | RW | O | AC Voltage Min Setting | AC voltage minimum setting used to adjust AC voltage maximum rating.
29 |  | VarMaxInj |  |  | uint16 |  |  | Var | RW | O | Reactive Power Injected Setting | Maximum injected reactive power setting used to adjust maximum injected reactive power rating.
30 |  | VarMaxAbs |  |  | uint16 |  |  | Var | RW | O | Reactive Power Absorbed Setting | Maximum absorbed reactive power setting used to adjust maximum absorbed reactive power rating.
31 |  | WChaRteMax |  |  | uint16 |  |  | W | RW | O | Charge Rate Max Setting | Maximum active power charge rate setting used to adjust maximum active power charge rate rating.
32 |  | WDisChaRteMax |  |  | uint16 |  |  | W | RW | O | Discharge Rate Max Setting | Maximum active power discharge rate setting used to adjust maximum active power discharge rate rating.
33 |  | VAChaRteMax |  |  | uint16 |  |  | VA | RW | O | Charge Rate Max VA Setting | Maximum apparent power charge rate setting used to adjust maximum apparent power charge rate rating.
34 |  | VADisChaRteMax |  |  | uint16 |  |  | VA | RW | O | Discharge Rate Max VA Setting | Maximum apparent power discharge rate setting used to adjust maximum apparent power discharge rate rating.
Scale Factors
35 |  | W_SF |  |  | sunssf |  |  |  | R | O | Active Power Scale Factor | Active power scale factor.
36 |  | PF_SF |  |  | sunssf |  |  |  | R | O | Power Factor Scale Factor | Power factor scale factor.
37 |  | VA_SF |  |  | sunssf |  |  |  | R | O | Apparent Power Scale Factor | Apparent power scale factor.
38 |  | Var_SF |  |  | sunssf |  |  |  | R | O | Reactive Power Scale Factor | Reactive power scale factor.
39 |  | V_SF |  |  | sunssf |  |  |  | R | O | Voltage Scale Factor | Voltage scale factor.
40 |  | A_SF |  |  | sunssf |  |  |  | R | O | Current Scale Factor | Current scale factor.

## 703
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | Access (R/RW) | Mandatory (M/O) | Label | Description | Detailed Description
|  | DEREnterService | [8 empty] | Enter Service | Enter service.
0 |  | ID | 703 |  | uint16 |  |  |  | R | M | Enter Service ID | Enter service model id.
1 |  | L | 12 |  | uint16 |  |  |  | RW | M | Enter Service Length | Enter service model length.
2 |  | ES |  |  | enum16 |  |  |  | RW | O | Permit Enter Service | Permit enter service.
|  | DISABLED | 0
|  | ENABLED | 1
3 |  | ESVHi |  |  | uint16 |  | V_SF | Pct | RW | O | Enter Service Voltage High | Enter service voltage high threshold as percent of normal voltage.
4 |  | ESVLo |  |  | uint16 |  | V_SF | Pct | RW | O | Enter Service Voltage Low | Enter service voltage low threshold as percent of normal voltage.
5 |  | ESHzHi |  |  | uint16 |  | Hz_SF | Hz | RW | O | Enter Service Frequency High | Enter service frequency high threshold.
6 |  | ESHzLo |  |  | uint16 |  | Hz_SF | Hz | RW | O | Enter Service Frequency Low | Enter service frequency low threshold.
7 |  | ESDlyTms |  |  | uint16 |  |  | Secs | RW | O | Enter Service Delay Time | Enter service delay time in seconds.
8 |  | ESRndTms |  |  | uint16 |  |  | Secs | RW | O | Enter Service Random Delay | Enter service random delay in seconds.
9 |  | ESRmpTms |  |  | uint16 |  |  | Secs | RW | O | Enter Service Ramp Time | Enter service ramp time in seconds.
10 |  | V_SF |  |  | sunssf |  |  |  | R | O | Voltage Scale Factor | Voltage scale factor.
11 |  | Hz_SF |  |  | sunssf |  |  |  | R | O | Frequency Scale Factor | Frequency scale factor.

## 704
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | Access (R/RW) | Mandatory (M/O) | Label | Description | Detailed Description
|  | DERCtlAC | [8 empty] | DER AC Controls | DER AC controls model.
0 |  | ID | 704 |  | uint16 |  |  |  | R | M | Model ID | Model name model id.
1 |  | L |  |  | uint16 |  |  |  | R | M | Model Length | Model name model length.
Set power factor when injecting active power
2 |  | PFWInjEna |  |  | enum16 |  |  |  | RW | O | Power Factor Enable (W Inj) Enable | Power factor enable when injecting active power.
|  | DISABLED | 0 | [7 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [7 empty] | Enabled | Function is enabled.
3 |  | PFWInjEnaRvrt |  |  | uint16 |  |  |  | R | O
|  | DISABLED | 0 | [7 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [7 empty] | Enabled | Function is enabled.
4 |  | PFWInjRvrtTms |  |  | uint32 |  |  | Secs | RW | O | PF Reversion Time (W Inj) | Power factor reversion timer when injecting active power.
6 |  | PFWInjRvrtRem |  |  | uint32 |  |  | Secs | R | O | PF Reversion Time Rem (W Inj) | Power factor reversion time remaining when injecting active power.
Set power factor when absorbing active power
8 |  | PFWAbsEna |  |  | enum16 |  |  |  | RW | O | Power Factor Enable (W Abs) Enable | Power factor enable when absorbing active power.
|  | DISABLED | 0 | [7 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [7 empty] | Enabled | Function is enabled.
9 |  | PFWAbsEnaRvrt |  |  | uint16 |  |  |  | R | O
|  | DISABLED | 0 | [7 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [7 empty] | Enabled | Function is enabled.
10 |  | PFWAbsRvrtTms |  |  | uint32 |  |  | Secs | RW | O | PF Reversion Time (W Abs) | Power factor reversion timer when absorbing active power.
12 |  | PFWAbsRvrtRem |  |  | uint32 |  |  | Secs | R | O | PF Reversion Time Rem (W Abs) | Power factor reversion time remaining when absorbing active power.
Limit maximum active power generation
14 |  | WMaxLimEna |  |  | enum16 |  |  |  | RW | O | Limit Max Active Power Enable | Limit maximum active power enable.
|  | DISABLED | 0 | [7 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [7 empty] | Enabled | Function is enabled.
15 |  | WMaxLim |  |  | uint16 |  | WMaxLim_SF | Pct | RW | O | Limit Max Power Setpoint | Limit maximum active power value.
16 |  | WMaxLimRvrt |  |  | uint16 |  | WMaxLim_SF | Pct | RW | O | Reversion Limit Max Power | Reversion limit maximum active power value.
17 |  | WMaxLimEnaRvrt |  |  | uint16 |  |  |  | R | O
|  | DISABLED | 0 | [7 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [7 empty] | Enabled | Function is enabled.
18 |  | WMaxLimRvrtTms |  |  | uint32 |  |  | Secs | RW | O | Limit Max Power Reversion Time | Limit maximum active power reversion time.
20 |  | WMaxLimRvrtRem |  |  | uint32 |  |  | Secs | R | O | Limit Max Power Rev Time Rem | Limit maximum active power reversion time remaining.
Set active power level (may be negative for charging)
22 |  | WSetEna |  |  | uint16 |  |  |  | RW | O | Set Active Power Enable | Set active power enable.
|  | DISABLED | 0 | [7 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [7 empty] | Enabled | Function is enabled.
23 |  | WSetMod |  |  | enum16 |  |  |  | RW | O | Set Active Power Mode | Set active power mode.
|  | W_MAX_PCT | 1 | [7 empty] | Active Power As Max Percent | Active power setting is percentage of maximum active power.
|  | WATTS | 2 | [7 empty] | Active Power As Watts | Active power setting is in watts.
24 |  | WSet |  |  | int32 |  | WSet_SF | W | RW | O | Active Power Setpoint (W) | Active power setting value in watts.
26 |  | WSetRvrt |  |  | int32 |  | WSet_SF | W | RW | O | Reversion Active Power (W) | Reversion active power setting value in watts.
28 |  | WSetPct |  |  | int32 |  | WSetPct_SF | Pct | RW | O | Active Power Setpoint (Pct) | Active power setting value as percent.
30 |  | WSetPctRvrt |  |  | int32 |  | WSetPct_SF | Pct | RW | O | Reversion Active Power (Pct) | Reversion active power setting value as percent.
32 |  | WSetEnaRvrt |  |  | uint16 |  |  |  | R | O
|  | DISABLED | 0 | [7 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [7 empty] | Enabled | Function is enabled.
33 |  | WSetRvrtTms |  |  | uint32 |  |  | Secs | RW | O | Active Power Reversion Time | Set active power reversion time.
35 |  | WSetRvrtRem |  |  | uint32 |  |  | Secs | R | O | Active Power Rev Time Rem | Set active power reversion time remaining.
Set reacitve power level
37 |  | VarSetEna |  |  | enum16 |  |  |  | RW | O | Set Reactive Power Enable | Set reactive power enable.
|  | DISABLED | 0 | [7 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [7 empty] | Enabled | Function is enabled.
38 |  | VarSetMod |  |  | enum16 |  |  |  | RW | O | Set Reactive Power Mode | Set reactive power mode.
|  | W_MAX_PCT | 1 | [7 empty] | Reactive Power as Watt Max Pct | Reactive power setting is percent of maximum active power.
|  | VAR_MAX_PCT | 2 | [7 empty] | Reactive Power as Var Max Pct | Reactive power setting is percent of maximum reactive power.
|  | VAR_AVAIL_PCT | 3 | [7 empty] | Reactive Power as Var Avail Pct | Reactive power setting is percent of available reactive power.
|  | VARS | 4 | [7 empty] | Reactive Power as Vars | Reactive power is in watts.
39 |  | VarSetPri |  |  | enum16 |  |  |  | R | O
|  | ACTIVE | 1
|  | REACTIVE | 2
40 |  | VarSet |  |  | int32 |  | VarSet_SF | Var | RW | O | Reactive Power Setpoint (Vars) | Reactive power setting value in vars.
42 |  | VarSetRvrt |  |  | int32 |  | VarSet_SF | Var | RW | O | Reversion Reactive Power (Vars) | Reversion reactive power setting value in vars.
44 |  | VarSetPct |  |  | int32 |  | VarSetPct_SF | Pct | RW | O | Reactive Power Setpoint (Pct) | Reactive power setting value as percent.
46 |  | VarSetPctRvrt |  |  | int32 |  | VarSetPct_SF | Pct | RW | O | Reversion Reactive Power (Pct) | Reversion reactive power setting value as percent.
|  | DISABLED | 0 | [7 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [7 empty] | Enabled | Function is enabled.
48 |  | VarSetRvrtTms |  |  | uint32 |  |  | Secs | RW | O | Reactive Power Reversion Time | Set reactive power reversion time.
50 |  | VarSetRvrtRem |  |  | uint32 |  |  | Secs | R | O | Reactive Power Rev Time Rem | Set reactive power reversion time remaining.
Scale factors
52 |  | PF_SF |  |  | sunssf |  |  |  | R | O | Power Factor Scale Factor | Power factor scale factor.
53 |  | WMaxLim_SF |  |  | sunssf |  |  |  | R | O | Limit Max Power Scale Factor | Limit maximum power scale factor.
54 |  | WSet_SF |  |  | sunssf |  |  |  | R | O | Active Power Scale Factor | Active power scale factor.
55 |  | WSetPct_SF |  |  | sunssf |  |  |  | R | O | Active Power Pct Scale Factor | Active power pct scale factor.
56 |  | VarSet_SF |  |  | sunssf |  |  |  | R | O | Reactive Power Scale Factor | Reactive power scale factor.
57 |  | VarSetPct_SF |  |  | sunssf |  |  |  | R | O | Reactive Power Pct Scale Factor | Reactive power pct scale factor.
Number of points in groups
58 |  | NPt |  |  | uint16 |  |  |  | R | M | Number of Points | Number of curve points supported.
59 |  | NCtl |  |  | uint16 |  |  |  | R | M | AC Power Factors | Number of AC Power Factors
AC Power Factors
|  | DERCtlAC.Ctl |  | NCtl | [6 empty] | DER AC Power Factors
AC Power Factor points
|  | DERCtlAC.Ctl.PFWInj | [8 empty] | Power Factor (W Inj)
| 0 | ActPt |  |  | uint16 |  |  |  | R | O
|  | DERCtlAC.Ctl.PFWInj.Pt |  | NPt
| 0 | PF |  |  | uint16 |  | PF_SF |  | RW | O | Power Factor (W Inj) | Power factor setpoint when injecting active power.
| 1 | Ext |  |  | enum32 |  |  |  | R | O | Power Factor Excitation (W Inj) | Power factor excitation setpoint when injecting active power.
|  | OVER_EXCITED | 0 | [7 empty] | Over-excited | Power factor over-excited excitation.
|  | UNDER_EXCITED | 1 | [7 empty] | Under-excited | Power factor under-excited excitation.
|  | DERCtlAC.Ctl.PFWInj.Pt |  | NPt
| 0 | PF |  |  | uint16 |  | PF_SF |  | RW | O | Reversion Power Factor (W Abs) | Reversion power factor setpoint when absorbing active power.
| 1 | Ext |  |  | enum32 |  |  |  | R | O | Reversion PF Excitation (W Abs) | Reversion power factor excitation setpoint when absorbing active power.
|  | OVER_EXCITED | 0 | [7 empty] | Over-excited | Power factor over-excited excitation.
|  | UNDER_EXCITED | 1 | [7 empty] | Under-excited | Power factor under-excited excitation.
|  | DERCtlAC.Ctl.PFWInjRvrt | [8 empty] | Reversion Power Factor (W Inj)
| 0 | ActPt |  |  | uint16 |  |  |  | R | O
|  | DERCtlAC.Ctl.PFWInjRvrt.Pt |  | NPt
| 0 | PF |  |  | uint16 |  | PF_SF |  | RW | O | Reversion Power Factor (W Inj) | Reversion power factor setpoint when injecting active power.
| 1 | Ext |  |  | enum32 |  |  |  | R | O | Reversion PF Excitation (W Inj) | Reversion power factor excitation setpoint when injecting active power.
|  | OVER_EXCITED | 0 | [7 empty] | Over-excited | Power factor over-excited excitation.
|  | UNDER_EXCITED | 1 | [7 empty] | Under-excited | Power factor under-excited excitation.
|  | DERCtlAC.Ctl.PFWAbs | [8 empty] | Power Factor (W Abs)
| 0 | ActPt |  |  | uint16 |  |  |  | R | O
|  | DERCtlAC.Ctl.PFWAbs.Pt |  | NPt
| 0 | PF |  |  | uint16 |  | PF_SF |  | RW | O | Power Factor (W Abs) | Power factor setpoint when absorbing active power.
| 1 | Ext |  |  | enum32 |  |  |  | R | O | Power Factor Excitation (W Abs) | Power factor excitation setpoint when absorbing active power.
|  | OVER_EXCITED | 0 | [7 empty] | Over-excited | Power factor over-excited excitation.
|  | UNDER_EXCITED | 1 | [7 empty] | Under-excited | Power factor under-excited excitation.
|  | DERCtlAC.Ctl.PFWInj | [8 empty] | Reversion Power Factor (W Abs)
| 0 | ActPt |  |  | uint16 |  |  |  | R | O

## 705
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | Access (R/RW) | Mandatory (M/O) | Label | Description | Detailed Description
|  | DERVoltVar | [8 empty] | DER Volt-Var | DER Volt-Var model.
0 |  | ID | 705 |  | uint16 |  |  |  | R | M | Model ID | DER Volt-Var model id.
1 |  | L |  |  | uint16 |  |  |  | R | M | Model Length | DER Volt-Var model length.
2 |  | Ena |  |  | enum16 |  |  |  | RW | M | Module Enable | Is Volt-Var control active.
|  | DISABLED | 0 | [7 empty] | Disabled | Function is enabled.
|  | ENABLED | 1 | [7 empty] | Enabled | Function is disabled.
3 |  | CrvSt |  |  | enum16 |  |  |  | R | M | Active Curve State | Current active curve state.
|  | INACTIVE | 0 | [7 empty] | No active curve | No curve is currenly active.
|  | ACTIVE | 1 | [7 empty] | Active curve enabled | Active curve in effect.
4 |  | AdptCrvReq |  |  | uint16 |  |  |  | RW | M | Set active curve request | Set active curve. 0 = No active curve
5 |  | AdptCrvRslt |  |  | enum16 |  |  |  | R | M | Set active curve result | Result of last set active curve operation.
|  | IN_PROGRESS | 0 | [7 empty] | Update In Progress | Curve update in progress.
|  | COMPLETED | 1 | [7 empty] | Update Complete | Curve update completed successfully.
|  | FAILED | 2 | [7 empty] | Update Failed | Curve update failed.
6 |  | NPt |  |  | uint16 |  |  |  | R | M | Number of Points | Number of curve points supported.
7 |  | NCrv |  |  | uint16 |  |  |  | R | M | Stored Curve Count | Number of stored curves supported.
8 |  | RvrtTms |  |  | uint32 |  |  |  | RW | O | Reversion timeout | Reversion time in seconds. 0 = No reversion time
10 |  | RvrtRem |  |  | uint32 |  |  |  | R | O | Reversion time left | Reversion time remaining in seconds
12 |  | RvrtCrv |  |  | uint16 |  |  |  | RW | O | Reversion curve | Default curve after reversion timeout.
13 |  | V_SF |  |  | sunssf |  |  |  | R | M | Voltage Scale Factor | Scale factor for curve voltage points.
14 |  | DeptRef_SF |  |  | sunssf |  |  |  | R | M | Var Scale Factor | Scale factor for curve var points.
Stored curve sets - Number of curve sets contained in NCrv
|  | DERVoltVar.Crv |  | NCrv | [6 empty] | Stored Curves | Stored curve sets.
| 0 | ActPt |  |  | uint16 |  |  |  | RW | M | Active Points | Number of active points.
| 1 | DeptRef |  |  | enum16 |  |  |  | RW | M | Dependent Reference | Curve dependent reference.
|  | W_MAX_PCT | 1 | [7 empty] | Percent Max Watts
|  | VAR_MAX_PCT | 2 | [7 empty] | Percent Max Vars
|  | VAR_AVAL_PCT | 3 | [7 empty] | Percent Available Vars
| 2 | Pri |  |  | enum16 |  |  |  | R | O
|  | ACTIVE | 1
|  | REACTIVE | 2
| 3 | VRef |  |  | uint16 |  |  |  | RW | O | Vref adjustment | Vref adjustment as percentage.
| 4 | VRefAuto |  |  | bitfield16 |  |  |  | RW | O | Autonomous Vref Enable | Enable automonous vref
|  | ENABLED | 0 | [7 empty] | Enabled Flag | Enabled flag (Disabled = 0, Enabled = 1).
| 5 | VRefTms |  |  | uint16 |  |  |  | RW | O | Auto Vref Time Constant | Autonomous vref time constant.
| 6 | RspTms |  |  | uint16 |  |  |  | RW | O | Open Loop Response Time | Open loop response time.
| 7 | ReadOnly |  |  | enum16 |  |  |  | RW | O | Curve Access | Curve read-write access.
|  | RW | 0 | [7 empty] | Read-Write Access | Curve has read-write access.
|  | R | 1 | [7 empty] | Read-Only Access | Curve has read-only access.
Stored curve sets - curve points for each stored curve - Number of curve points contained in NPt
|  | DERVoltVar.Crv.Pt |  | NPt | [6 empty] | Stored Curve Points | Stored curve points.
| 0 | V |  |  | uint16 |  |  | VRefPct | RW | M | Voltage Point | Curve voltage point as percentage.
| 1 | Var |  |  | int16 |  | DeptRef_SF | VarPct | RW | M | Reactive Power Point | Curve reactive power point as set in DeptRef point.

## 706
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | Access (R/RW) | Mandatory (M/O) | Label | Description | Detailed Description
|  | DERVoltWatt | [8 empty] | DERVolt-Watt | DER Volt-Watt model.
0 |  | ID | 706 |  | uint16 |  |  |  | R | M | Model ID | DER Volt-Watt model id.
1 |  | L |  |  | uint16 |  |  |  | R | M | Model Length | DER Volt-Watt model length.
2 |  | Ena |  |  | bitfield16 |  |  |  | RW | M | Module Enable | Is Volt-Watt control active.
|  | ENABLED | 0 | [7 empty] | Enabled Flag | Enabled flag (Disabled = 0, Enabled = 1).
3 |  | AdoptCrv |  |  | uint16 |  |  |  | RW | M | Adopt Curve | Index of curve points to adopt. First curve index is 1.
4 |  | AdoptCrvRslt |  |  | enum16 |  |  |  | R | M | Adopt Curve Result | Result of last adopt curve operation.
|  | IN_PROGRESS | 0 | [7 empty] | Update In Progress | Curve update in progress.
|  | COMPLETED | 1 | [7 empty] | Update Complete | Curve update completed successfully.
|  | FAILED | 2 | [7 empty] | Update Failed | Curve update failed.
5 |  | NPt |  |  | uint16 |  |  |  | R | M | Number of Points | Number of curve points supported.
6 |  | NCrv |  |  | uint16 |  |  |  | R | M | Stored Curve Count | Number of stored curves supported.
7 |  | Pad |  |  | pad |  |  |  | R | O | Allignment Pad | Pad field for alignment.
8 |  | V_SF |  |  | sunssf |  |  |  | R | M | Voltage Scale Factor | Scale factor for curve voltage points.
9 |  | DeptRef_SF |  |  | sunssf |  |  |  | R | M | Watt Scale Factor | Scale factor for curve watt points.
Stored curve sets - Number of curve sets contained in NCrv
|  | DERVoltWatt.Crv |  | NCrv | [6 empty] | Stored Curves | Stored curve sets.
| 0 | ActPt |  |  | uint16 |  |  |  | RW | M | Active Points | Number of active points.
| 1 | DeptRef |  |  | enum16 |  |  |  | RW | M | Dependent Reference | Curve dependent reference.
|  | W_MAX_PCT | 1
|  | W_AVAL_PCT | 2
| 2 | RspTms |  |  | uint16 |  |  |  | RW | O | Open Loop Response Time | Open loop response time.
| 3 | ReadOnly |  |  | enum16 |  |  |  | RW | O | Curve Access | Curve read-write access.
|  | RW | 0 | [7 empty] | Read-Write Access | Curve has read-write access.
|  | R | 1 | [7 empty] | Read-Only Access | Curve has read-only access.
Stored curve sets - curve points for each stored curve - Number of curve points contained in NPt
|  | DERVoltWatt.Crv.Pt |  | NPt | [6 empty] | Stored Curve Points | Stored curve points.
| 0 | V |  |  | uint16 |  | V_SF | VRefPct | RW | M | Voltage Point | Curve voltage point as percentage.
| 1 | W |  |  | int16 |  | DeptRef_SF | DeptRef | RW | M | Dependent Reference | Curve time point in seconds.

## 707
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | Access (R/RW) | Mandatory (M/O) | Label | Description | Detailed Description
|  | DERTripLV | [8 empty] | DER Trip LV | DER Low voltage trip model.
0 |  | ID | 707 |  | uint16 |  |  |  | R | M | DER Trip LV Model ID | DER low voltage trip model id.
1 |  | L |  |  | uint16 |  |  |  | R | M | DER Trip LV Model Length | DER low volatage trip model length.
2 |  | ModEna |  |  | bitfield16 |  |  |  | RW | M | DER Trip LV Module Enable | Is DER low voltage trip control active.
|  | ENABLED | 0 | [7 empty] | Enabled Flag | Enabled flag (Disabled = 0, Enabled = 1).
3 |  | AdoptCrv |  |  | uint16 |  |  |  | RW | M | Adopt Curve | Index of curve points to adopt. First curve index is 1.
4 |  | AdoptCrvRslt |  |  | enum16 |  |  |  | R | M | Adopt Curve Result | Result of last adopt curve operation.
|  | IN_PROGRESS | 0 | [7 empty] | Update In Progress | Curve update in progress.
|  | COMPLETED | 1 | [7 empty] | Update Complete | Curve update completed successfully.
|  | FAILED | 2 | [7 empty] | Update Failed | Curve update failed.
5 |  | NPt |  |  | uint16 |  |  |  | R | M | Number of Points | Number of curve points supported.
6 |  | NCrv |  |  | uint16 |  |  |  | R | M | Stored Curve Count | Number of stored curves supported.
7 |  | V_SF |  |  | sunssf |  |  |  | R | M | Voltage Scale Factor | Scale factor for curve voltage points.
8 |  | Tms_SF |  |  | sunssf |  |  |  | R | M | Time Point Scale Factor | Scale factor for curve time points.
Stored curve sets - Number of curve sets contained in NCrv
|  | DERTripLV.Crv |  | NCrv | [6 empty] | Stored Curves | Stored curve sets.
Stored curve set containing a Must Trip, May Trip, and Momentary Cessation Curve - Number of curve points contained in NPt
|  | DERTripLV.Crv.MustTrip | [8 empty] | Must Trip Curve | Stored must trip curve.
| 0 | ActPt |  |  | uint16 |  |  |  | R | O | Number of Active Points | Number of active points in must trip curve.
|  | DERTripLV.Crv.MustTrip.Pt |  | NPt | [6 empty] | Must Trip Curve Points | Must trip curve points.
| 0 | V |  |  | uint16 |  | V_SF | VRefPct | R | M | Voltage Point | Curve voltage point as percentage.
| 1 | Tms |  |  | uint16 |  | Tms_SF | Secs | R | M | Time Point | Curve time point in seconds.
|  | DERTripLV.Crv.MayTrip | [8 empty] | May Trip Curve | Stored may trip curve.
| 0 | ActPt |  |  | uint16 |  |  |  | R | O | Number of Active Points | Number of active points in may trip curve.
|  | DERTripLV.Crv.MayTrip.Pt |  | NPt | [6 empty] | May Trip Curve Points | May trip curve points.
| 0 | V |  |  | uint16 |  | V_SF | VRefPct | R | M | Voltage Point | Curve voltage point as percentage.
| 1 | Tms |  |  | uint16 |  | Tms_SF | Secs | R | M | Time Point | Curve time point in seconds.
|  | DERTripLV.Crv.MomCess | [8 empty] | Momentary Cessation Curve | Stored momentary cessation curve.
| 0 | ActPt |  |  | uint16 |  |  |  | R | O | Number of Active Points | Number of active points in the momentary cessation curve.
|  | DERTripLV.Crv.MomCess.Pt |  | NPt | [6 empty] | Mom Cessation Curve Points | Monetary cessation curve points.
| 0 | V |  |  | uint16 |  | V_SF | VRefPct | R | M | Voltage Point | Curve voltage point as percentage.
| 1 | Tms |  |  | uint16 |  | Tms_SF | Secs | R | M | Time Point | Curve time point in seconds.

## 708
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | Access (R/RW) | Mandatory (M/O) | Label | Description | Detailed Description
|  | DERTripHV | [8 empty] | DER Trip HV | DER high voltage trip model.
0 |  | ID | 708 |  | uint16 |  |  |  | R | M | DER Trip HV Model ID | DER high voltage trip model id.
1 |  | L |  |  | uint16 |  |  |  | R | M | DER Trip HV Model Length | DER high voltage trip model length.
2 |  | ModEna |  |  | bitfield16 |  |  |  | RW | M | DER Trip HV Module Enable | Is DER high voltage trip control active.
|  | ENABLED | 0 | [7 empty] | Enabled Flag | Enabled flag (Disabled = 0, Enabled = 1).
3 |  | AdoptCrv |  |  | uint16 |  |  |  | RW | M | Adopt Curve | Index of curve points to adopt. First curve index is 1.
4 |  | AdoptCrvRslt |  |  | enum16 |  |  |  | R | M | Adopt Curve Result | Result of last adopt curve operation.
|  | IN_PROGRESS | 0 | [7 empty] | Update In Progress | Curve update in progress.
|  | COMPLETED | 1 | [7 empty] | Update Complete | Curve update completed successfully.
|  | FAILED | 2 | [7 empty] | Update Failed | Curve update failed.
5 |  | NPt |  |  | uint16 |  |  |  | R | M | Number of Points | Number of curve points supported.
6 |  | NCrv |  |  | uint16 |  |  |  | R | M | Stored Curve Count | Number of stored curves supported.
7 |  | V_SF |  |  | sunssf |  |  |  | R | M | Voltage Scale Factor | Scale factor for curve voltage points.
8 |  | Tms_SF |  |  | sunssf |  |  |  | R | M | Time Point Scale Factor | Scale factor for curve time points.
Stored curve sets - Number of curve sets contained in NCrv
|  | DERTripHV.Crv |  | NCrv | [6 empty] | Stored Curves | Stored curve sets.
Stored curve set containing a Must Trip, May Trip, and Momentary Cessation Curve - Number of curve points contained in NPt
|  | DERTripHV.Crv.MustTrip | [8 empty] | Must Trip Curve | Stored must trip curve.
| 0 | ActPt |  |  | uint16 |  |  |  | R | O | Number of Active Points | Number of active points in must trip curve.
|  | DERTripHV.Crv.MustTrip.Pt |  | NPt | [6 empty] | Must Trip Curve Points | Must trip curve points.
| 0 | V |  |  | uint16 |  | V_SF | VRefPct | R | M | Voltage Point | Curve voltage point as percentage.
| 1 | Tms |  |  | uint16 |  | Tms_SF | Secs | R | M | Time Point | Curve time point in seconds.
|  | DERTripHV.Crv.MayTrip | [8 empty] | May Trip Curve | Stored may trip curve.
| 0 | ActPt |  |  | uint16 |  |  |  | R | O | Number of Active Points | Number of active points in may trip curve.
|  | DERTripHV.Crv.MayTrip.Pt |  | NPt | [6 empty] | May Trip Curve Points | May trip curve points.
| 0 | V |  |  | uint16 |  | V_SF | VRefPct | R | M | Voltage Point | Curve voltage point as percentage.
| 1 | Tms |  |  | uint16 |  | Tms_SF | Secs | R | M | Time Point | Curve time point in seconds.
|  | DERTripHV.Crv.MomCess | [8 empty] | Momentary Cessation Curve | Stored momentary cessation curve.
| 0 | ActPt |  |  | uint16 |  |  |  | R | O | Number of Active Points | Number of active points in the momentary cessation curve.
|  | DERTripHV.Crv.MomCess.Pt |  | NPt | [6 empty] | Mom Cessation Curve Points | Monetary cessation curve points.
| 0 | V |  |  | uint16 |  | V_SF | VRefPct | R | M | Voltage Point | Curve voltage point as percentage.
| 1 | Tms |  |  | uint16 |  | Tms_SF | Secs | R | M | Time Point | Curve time point in seconds.

## 709
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | Access (R/RW) | Mandatory (M/O) | Label | Description | Detailed Description
|  | DERTripLF | [8 empty] | DER Trip LF | DER low frequency trip model.
0 |  | ID | 709 |  | uint16 |  |  |  | R | M | DER Trip LF Model ID | DER low frequency trip model id.
1 |  | L |  |  | uint16 |  |  |  | R | M | DER Trip LF Model Length | DER low frequency trip model length.
2 |  | ModEna |  |  | bitfield16 |  |  |  | RW | M | DER Trip LF Module Enable | Is DER low frequency trip control active.
|  | ENABLED | 0 | [7 empty] | Enabled Flag | Enabled flag (Disabled = 0, Enabled = 1).
3 |  | AdoptCrv |  |  | uint16 |  |  |  | RW | M | Adopt Curve | Index of curve points to adopt. First curve index is 1.
4 |  | AdoptCrvRslt |  |  | enum16 |  |  |  | R | M | Adopt Curve Result | Result of last adopt curve operation.
|  | IN_PROGRESS | 0 | [7 empty] | Update In Progress | Curve update in progress.
|  | COMPLETED | 1 | [7 empty] | Update Complete | Curve update completed successfully.
|  | FAILED | 2 | [7 empty] | Update Failed | Curve update failed.
5 |  | NPt |  |  | uint16 |  |  |  | R | M | Number of Points | Number of curve points supported.
6 |  | NCrv |  |  | uint16 |  |  |  | R | M | Stored Curve Count | Number of stored curves supported.
7 |  | Freq_SF |  |  | sunssf |  |  |  | R | M | Frequency Scale Factor | Scale factor for curve frequency points.
8 |  | Tms_SF |  |  | sunssf |  |  |  | R | M | Time Point Scale Factor | Scale factor for curve time points.
Stored curve sets - Number of curve sets contained in NCrv
|  | DERTripLF.Crv |  | NCrv | [6 empty] | Stored Curves | Stored curve sets.
Stored curve set containing a Must Trip, May Trip, and Momentary Cessation Curve - Number of curve points contained in NPt
|  | DERTripLF.Crv.MustTrip | [8 empty] | Must Trip Curve | Stored must trip curve.
| 0 | ActPt |  |  | uint16 |  |  |  | R | O | Number of Active Points | Number of active points in must trip curve.
|  | DERTripLF.Crv.MustTrip.Pt |  | NPt | [6 empty] | Must Trip Curve Points | Must trip curve points.
| 0 | Freq |  |  | uint16 |  | Freq_SF | Hz | R | M | Frequency Point | Curve frequency point.
| 1 | Tms |  |  | uint16 |  | Tms_SF | Secs | R | M | Time Point | Curve time point in seconds.
|  | DERTripLF.Crv.MayTrip | [8 empty] | May Trip Curve | Stored may trip curve.
| 0 | ActPt |  |  | uint16 |  |  |  | R | O | Number of Active Points | Number of active points in may trip curve.
|  | DERTripLF.Crv.MayTrip.Pt |  | NPt | [6 empty] | May Trip Curve Points | May trip curve points.
| 0 | Freq |  |  | uint16 |  | Freq_SF | Hz | R | M | Frequency Point | Curve frequency point.
| 1 | Tms |  |  | uint16 |  | Tms_SF | Secs | R | M | Time Point | Curve time point in seconds.
|  | DERTripLF.Crv.MomCess | [8 empty] | Momentary Cessation Curve | Stored momentary cessation curve.
| 0 | ActPt |  |  | uint16 |  |  |  | R | O | Number of Active Points | Number of active points in the momentary cessation curve.
|  | DERTripLF.Crv.MomCess.Pt |  | NPt | [6 empty] | Mom Cessation Curve Points | Monetary cessation curve points.
| 0 | Freq |  |  | uint16 |  | Freq_SF | Hz | R | M | Frequency Point | Curve frequency point.
| 1 | Tms |  |  | uint16 |  | Tms_SF | Secs | R | M | Time Point | Curve time point in seconds.

## 710
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | Access (R/RW) | Mandatory (M/O) | Label | Description | Detailed Description
|  | DERTripHF | [8 empty] | DER Trip HF | DER high frequency trip model.
0 |  | ID | 710 |  | uint16 |  |  |  | R | M | DER Trip HFModel ID | DER high frequency trip model id.
1 |  | L |  |  | uint16 |  |  |  | R | M | DER Trip HFModel Length | DER high frequency trip model length.
2 |  | ModEna |  |  | bitfield16 |  |  |  | RW | M | DER Trip HFModule Enable | Is DER high frequency trip control active.
|  | ENABLED | 0 | [7 empty] | Enabled Flag | Enabled flag (Disabled = 0, Enabled = 1).
3 |  | AdoptCrv |  |  | uint16 |  |  |  | RW | M | Adopt Curve | Index of curve points to adopt. First curve index is 1.
4 |  | AdoptCrvRslt |  |  | enum16 |  |  |  | R | M | Adopt Curve Result | Result of last adopt curve operation.
|  | IN_PROGRESS | 0 | [7 empty] | Update In Progress | Curve update in progress.
|  | COMPLETED | 1 | [7 empty] | Update Complete | Curve update completed successfully.
|  | FAILED | 2 | [7 empty] | Update Failed | Curve update failed.
5 |  | NPt |  |  | uint16 |  |  |  | R | M | Number of Points | Number of curve points supported.
6 |  | NCrv |  |  | uint16 |  |  |  | R | M | Stored Curve Count | Number of stored curves supported.
7 |  | Freq_SF |  |  | sunssf |  |  |  | R | M | Frequency Scale Factor | Scale factor for curve frequency points.
8 |  | Tms_SF |  |  | sunssf |  |  |  | R | M | Time Point Scale Factor | Scale factor for curve time points.
Stored curve sets - Number of curve sets contained in NCrv
|  | DERTripHF.Crv |  | NCrv | [6 empty] | Stored Curves | Stored curve sets.
Stored curve set containing a Must Trip, May Trip, and Momentary Cessation Curve - Number of curve points contained in NPt
|  | DERTripHF.Crv.MustTrip | [8 empty] | Must Trip Curve | Stored must trip curve.
| 0 | ActPt |  |  | uint16 |  |  |  | R | O | Number of Active Points | Number of active points in must trip curve.
|  | DERTripHF.Crv.MustTrip.Pt |  | NPt | [6 empty] | Must Trip Curve Points | Must trip curve points.
| 0 | Freq |  |  | uint16 |  | Freq_SF | Hz | R | M | Frequency Point | Curve frequency point.
| 1 | Tms |  |  | uint16 |  | Tms_SF | Secs | R | M | Time Point | Curve time point in seconds.
|  | DERTripHF.Crv.MayTrip | [8 empty] | May Trip Curve | Stored may trip curve.
| 0 | ActPt |  |  | uint16 |  |  |  | R | O | Number of Active Points | Number of active points in may trip curve.
|  | DERTripHF.Crv.MayTrip.Pt |  | NPt | [6 empty] | May Trip Curve Points | May trip curve points.
| 0 | Freq |  |  | uint16 |  | Freq_SF | Hz | R | M | Frequency Point | Curve frequency point.
| 1 | Tms |  |  | uint16 |  | Tms_SF | Secs | R | M | Time Point | Curve time point in seconds.
|  | DERTripHF.Crv.MomCess | [8 empty] | Momentary Cessation Curve | Stored momentary cessation curve.
| 0 | ActPt |  |  | uint16 |  |  |  | R | O | Number of Active Points | Number of active points in the momentary cessation curve.
|  | DERTripHF.Crv.MomCess.Pt |  | NPt | [6 empty] | Mom Cessation Curve Points | Monetary cessation curve points.
| 0 | Freq |  |  | uint16 |  | Freq_SF | Hz | R | M | Frequency Point | Curve frequency point.
| 1 | Tms |  |  | uint16 |  | Tms_SF | Secs | R | M | Time Point | Curve time point in seconds.

## 711
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | Access (R/RW) | Mandatory (M/O) | Label | Description | Detailed Description
|  | DERFreqDroop | [8 empty] | DER Frequency Droop | DER Frequency Droop model.
0 |  | ID | 711 |  | uint16 |  |  |  | R | M | DER Frequency Droop ID | DER Frequency Droop model id.
1 |  | L |  |  | uint16 |  |  |  | R | M | DER Frequency Droop Length | DER Frequency Droop model length.
2 |  | ModEna |  |  | enum16 |  |  |  | RW | M |  | Is DER Frequency-Watt (Frequency-Droop) control active.
|  | DISABLED | 0
|  | ENABLED | 1
3 |  | DbOf |  |  | uint16 |  | Db_SF | Hz | RW | M | Over-frequency Deadband | The deadband value for over-frequency conditions in Hz.
4 |  | DbUf |  |  | uint16 |  | Db_SF | Hz | RW | M | Under-frequency Deadband | The deadband value for under-frequency conditions in Hz.
5 |  | KOf |  |  | uint16 |  | K_SF |  | RW | M | Over-frequency Change Ratio | Frequency droop per-unit frequency change for over-frequency conditions corresponding to 1 per-unit power output change.
6 |  | KUf |  |  | uint16 |  | K_SF |  | RW | M | Under-frequency Change Ratio | Frequency droop per-unit frequency change for under-frequency conditions corresponding to 1 per-unit power output change.
7 |  | RspTms |  |  | uint16 |  | RspTms_SF | Secs | RW | M | Open-Loop Response Time | The open-loop response time in seconds. | The duration from a step change in control signal input until the output changes by 90% of its final change, before any overshoot.
8 |  | Db_SF |  |  | sunssf |  |  |  | R | M | Deadband Scale Factor | Deadband scale factor.
9 |  | K_SF |  |  | sunssf |  |  |  | R | M | Frequency Change Scale Factor | Frequency change scale factor.
10 |  | RspTms_SF |  |  | sunssf |  |  |  | R | M | Open-Loop Scale Factor | Open loop response time scale factor.

## 712
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | Access (R/RW) | Mandatory (M/O) | Label | Description | Detailed Description
|  | DERWattVar | [8 empty] | DER Watt-Var | DER Watt-Var mod.
0 |  | ID | 712 |  | uint16 |  |  |  | R | M | Model ID | DER Watt-Var model id.
1 |  | L |  |  | uint16 |  |  |  | R | M | Model Length | DER Watt-Var model length.
2 |  | Ena |  |  | enum16 |  |  |  | RW | M | Module Enable | Is Watt-Var control active.
|  | DISABLED | 0 | [7 empty] | Disabled | Function is enabled.
|  | ENABLED | 1 | [7 empty] | Enabled | Function is disabled.
3 |  | CrvSt |  |  | enum16 |  |  |  | R | M | Active Curve State | Current active curve state.
|  | INACTIVE | 0 | [7 empty] | No active curve | No curve is currenly active.
|  | ACTIVE | 1 | [7 empty] | Active curve enabled | Active curve in effect.
4 |  | AdptCrvReq |  |  | uint16 |  |  |  | RW | M | Set active curve request | Set active curve. 0 = No active curve
5 |  | AdptCrvRslt |  |  | enum16 |  |  |  | R | M | Set active curve result | Result of last set active curve operation.
|  | IN_PROGRESS | 0 | [7 empty] | Update In Progress | Curve update in progress.
|  | COMPLETED | 1 | [7 empty] | Update Complete | Curve update completed successfully.
|  | FAILED | 2 | [7 empty] | Update Failed | Curve update failed.
6 |  | NPt |  |  | uint16 |  |  |  | R | M | Number of Points | Number of curve points supported.
7 |  | NCrv |  |  | uint16 |  |  |  | R | M | Stored Curve Count | Number of stored curves supported.
8 |  | RvrtTms |  |  | uint32 |  |  |  | RW | O | Reversion timeout | Reversion time in seconds. 0 = No reversion time
10 |  | RvrtRem |  |  | uint32 |  |  |  | R | O | Reversion time left | Reversion time remaining in seconds
12 |  | RvrtCrv |  |  | uint16 |  |  |  | RW | O | Reversion curve | Default curve after reversion timeout.
13 |  | DeptRef_SF |  |  | sunssf |  |  |  | R | M | Var Scale Factor | Scale factor for curve var points.
Stored curve sets - Number of curve sets contained in NCrv
|  | DERWattVar.Crv |  | NCrv | [6 empty] | Stored Curves | Stored curve sets.
| 0 | ActPt |  |  | uint16 |  |  |  | RW | M | Active Points | Number of active points.
| 1 | DeptRef |  |  | enum16 |  |  |  | RW | M | Dependent Reference | Curve dependent reference.
|  | W_MAX_PCT | 1 | [7 empty] | Percent Max Watts
|  | VAR_MAX_PCT | 2 | [7 empty] | Percent Max Vars
|  | VAR_AVAL_PCT | 3 | [7 empty] | Percent Available Vars
| 2 | Pri |  |  | enum16 |  |  |  | R | O
|  | ACTIVE | 1
|  | REACTIVE | 2
| 3 | ReadOnly |  |  | enum16 |  |  |  | RW | O | Curve Access | Curve read-write access.
|  | RW | 0 | [7 empty] | Read-Write Access | Curve has read-write access.
|  | R | 1 | [7 empty] | Read-Only Access | Curve has read-only access.
Stored curve sets - curve points for each stored curve - Number of curve points contained in NPt
|  | DERWattVar.Crv.Pt |  | NPt | [6 empty] | Stored Curve Points | Stored curve points.
| 0 | W |  |  | uint16 |  |  | VRefPct | RW | M | Active Power Point | Curve active power point as percentage.
| 1 | Var |  |  | int16 |  | DeptRef_SF | VarPct | RW | M | Reactive Power Point | Curve reactive power point as set in DeptRef point.

## 713
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | Access (R/RW) | Mandatory (M/O) | Label | Description | Detailed Description
|  | DERMeasureDC | [8 empty] | DER DC Measurement | DER DC measurement.
0 |  | ID | 713 |  | uint16 |  |  |  | R | M | DER DC Measure Model ID | DER DC measurement model id.
1 |  | L |  |  | uint16 |  |  |  | R | M | DER DC MeasureModel Length | DER DC measurement model length.
DC General
2 |  | Alrm |  |  | bitfield32 |  |  |  | R | O | Port Alarms | Bitfield of ports with active alarms. Bit is 1 if port has an active alarm. Bit 0 is first port.
4 |  | NPrt |  |  | uint16 |  |  |  | R | O | Number of Ports | Number of DC ports.
5 |  | DCA |  |  | int16 |  | DCA_SF |  | R | O | DC Current | Total DC current for all ports.
6 |  | DCW |  |  | int16 |  | DCW_SF |  | R | O | DC Power | Total DC power for all ports.
7 |  | DCWhInj |  |  | acc64 |  | DCWH_SF |  | R | O | DC Energy Injected | Total cumulative DC energy injected for all ports.
11 |  | DCWhAbs |  |  | acc64 |  | DCWH_SF |  | R | O | DC Energy Absorbed | Total cumulative DC energy absorbed for all ports.
15 |  | DCA_SF |  |  | sunssf |  |  |  | R | O | DC Current Scale Factor | DC current scale factor.
16 |  | DCV_SF |  |  | sunssf |  |  |  | R | O | DC Voltage Scale Factor | DC voltage scale factor.
17 |  | DCW_SF |  |  | sunssf |  |  |  | R | O | DC Power Scale Factor | DC power scale factor.
18 |  | DCWH_SF |  |  | sunssf |  |  |  | R | O | DC Energy Scale Factor | DC energy scale factor.
DC Port
|  | DERMeasureDC.Prt |  | NPrt
| 0 | PrtTyp |  |  | enum16 |  |  |  | R | O | Port Type | Port type.
|  | PV | 1 | [7 empty] | Photovoltaic
|  | ESS | 2 | [7 empty] | Energy Storage System
|  | EV | 3 | [7 empty] | Electric Vehicle
|  | INJ | 4 | [7 empty] | Generic Injecting
|  | ABS | 5 | [7 empty] | Generic Absorbing
|  | BIDIR | 6 | [7 empty] | Generic Bidirectional
| 1 | ID |  |  | uint16 |  |  |  | R | O | Port ID | Port ID.
| 2 | IDStr |  |  | string | 8 |  |  | R | O | Port ID String | Port ID string.
| 10 | DCA |  |  | int16 |  | DCA_SF |  | R | O | DC Current | DC current for the port.
| 11 | DCV |  |  | uint16 |  | DCV_SF |  | R | O | DC Voltage | DC voltage for the port.
| 12 | DCW |  |  | int16 |  | DCW_SF |  | R | O | DC Power | DC power for the port.
| 13 | DCWhInj |  |  | acc64 |  | DCWH_SF |  | R | O | DC Energy Injected | Total cumulative DC energy injected for the port.
| 17 | DCWhAbs |  |  | acc64 |  | DCWH_SF |  | R | O | DC Energy Absorbed | Total cumulative DC energy absorbed for the port.
| 21 | Tms |  |  | uint32 |  |  |  | R | O | DC Port Timer | DC port timer.
| 23 | Tmp |  |  | int16 |  |  |  | R | O | DC Port Temperature | DC port temerature.
| 24 | DCSt |  |  | enum16 |  |  |  | R | O | DC Port Status | DC port status.
| 25 | DCAlrm |  |  | bitfield32 |  |  |  | R | O | DC Port Alarm | DC port alarm.
|  | GROUND_FAULT | 0 | [7 empty] | Ground Fault
|  | INPUT_OVER_VOLTAGE | 1 | [7 empty] | Input Over Voltage
|  | RESERVED | 19 | [7 empty] | Reserved
|  | DC_DISCONNECT | 3 | [7 empty] | DC Disconnect
|  | CABINET_OPEN | 5 | [7 empty] | Cabinet Open
|  | MANUAL_SHUTDOWN | 6 | [7 empty] | Manual Shutdown
|  | OVER_TEMP | 7 | [7 empty] | Over Temperature
|  | BLOWN_FUSE | 12 | [7 empty] | Blown Fuse
|  | UNDER_TEMP | 13 | [7 empty] | Under Temperature
|  | MEMORY_LOSS | 14 | [7 empty] | Memory Loss
|  | ARC_DETECTION | 15 | [7 empty] | Arc Detection
|  | TEST_FAILED | 20 | [7 empty] | Test Failed
|  | INPUT_UNDER_VOLTAGE | 21 | [7 empty] | Under Voltage
|  | INPUT_OVER_CURRENT | 22 | [7 empty] | Over Current